## Node4.4-Metadata
Label | HazopMetadataTable4.4
Description | Table 4.4 This is a selection from the report that could result from the study. Enough has been included here to illustrate each of the main guidewords at least once. An action placed on two team members means that they are both expected to be involved in resolving the problem. However, the responsibility for the response is placed upon the ﬁrst named member.

## Node4.4-Analysis
Ref. | Deviation | Cause | Consequence | Safeguards | Action Ref. | Action | Action On
1 | No flow | Wrong initiating sequence used by the customer | Delay. Possible damage from wrong sequence. Sale may be lost. | Required sequence is usual for the UK and uses illuminated buttons on the pump panel. The site operator can select and speak to each station. | A1 | Consider installing an alert to the operator whenever delay between removing hose and start of pumping exceeds selected time (say 20 s). | PM
2 | No flow | Supply tank at low cutoff level | Delay and frustration for customer as cause not apparent. | Alarm to site operator of impending loss of supply. Operating procedure to cone off pumps with prepared signage. | A2 | Review restocking arrangements against the expected demands to minimize this situation. | SM
2 | No flow | Supply tank at low cutoff level | Delay and frustration for customer as cause not apparent. | Alarm to site operator of impending loss of supply. Operating procedure to cone off pumps with prepared signage. | A3 | Review operator training and testing. | HS
8 | More quantity | Customer error | Customer cannot pay; delay at till and at pump. | None | A5 | Cover in training procedures. | SM
9 | More (high) fuel flow | Dead man’s handle on pump fails or the flow fails to shut off on high level in tank | Fuel spillage over side of car, onto ground, and into drain system. Possible fire. | Maintenance of the pumps. Interceptor within the drains. | A6 | Check on the recommended maintenance procedures. | PM
9 | More (high) fuel flow | Dead man’s handle on pump fails or the flow fails to shut off on high level in tank | Fuel spillage over side of car, onto ground, and into drain system. Possible fire. | Maintenance of the pumps. Interceptor within the drains. | A6 | Check on the recommended maintenance procedures. | SM
9 | More (high) fuel flow | Dead man’s handle on pump fails or the flow fails to shut off on high level in tank | Fuel spillage over side of car, onto ground, and into drain system. Possible fire. | Maintenance of the pumps. Interceptor within the drains. | A7 | Check for level indicator and warning of interceptor overload. | HS
9 | More (high) fuel flow | Dead man’s handle on pump fails or the flow fails to shut off on high level in tank | Fuel spillage over side of car, onto ground, and into drain system. Possible fire. | Maintenance of the pumps. Interceptor within the drains. | A8 | Review location and effectiveness of the first aid firefighting facilities. | HS
10 | More time | Driver leaves car unattended (e.g., to shop in main store) | Pump blocked to other users. Uncertainty over “abandoned” vehicle. | None | A9 | Establish procedure to deal with “abandoned” vehicles including emergency evacuation of the area. | HS
13 | Less quantity | Low level in main supply tank | Customers cannot get fuel. | Low level warning on main supply tank. | A11 | Check that resupply arrangements cover all likely rates of sale. See also A2. | SM
13 | Less quantity | Low level in main supply tank | Customers cannot get fuel. | Operator training to cone off the affected pumps. | A12 | Review | SM
16 | Reverse entry of car into the pump lanes | Driver mistake or deliberate short cut taken | Confusion among other users and increased likelihood of on-site collision. | Signage | A13 | Review the position and instructions on signs. | SA
16 | Reverse entry of car into the pump lanes | Driver mistake or deliberate short cut taken | Confusion among other users and increased likelihood of on-site collision. | Signage | A13 | Review the position and instructions on signs. | SM
16 | Reverse entry of car into the pump lanes | Driver mistake or deliberate short cut taken | Confusion among other users and increased likelihood of on-site collision. | Signage | A14 | Consider if routing of entry/exit slip lanes can reduce occurrence. | SA
18 | As well as— customer uses mobile phone | Customer ignores warnings | Possible ignition source—not likely with diesel but could be with petrol. | Warning notice at every pump station. | A15 | Check on reality of the rumors of fuel ignition from mobile phones. | HS
18 | As well as— customer uses mobile phone | Customer ignores warnings | Possible ignition source—not likely with diesel but could be with petrol. | Warning notice at every pump station. | A16 | Consider requiring till operator to warn phone users over built in speakers on pump station. | SM
19 | Only part of sequence completed | Customer does not properly replace fuel nozzle on its stand | Transfer pump continues to run against closed valve. Payment cannot be made and customer must return to the pump. | Till operator can notify customer using the pump speaker but is unlikely to spot the problem before customer leaves the pump. | A17 | Check with manufacturer how likely this is with the chosen design and what the alternatives are. | SM
19 | Only part of sequence completed | Customer does not properly replace fuel nozzle on its stand | Transfer pump continues to run against closed valve. Payment cannot be made and customer must return to the pump. | Till operator can notify customer using the pump speaker but is unlikely to spot the problem before customer leaves the pump. | A17 | Check with manufacturer how likely this is with the chosen design and what the alternatives are. | PM
21 | Other fuel container filled | Customer uses fuel can (perhaps as well as filling car fuel tank) | Pump is stopped and then restarted. May attempt to pump a different fuel. High-level cutoff may not work if container has a wide neck. | Not possible to pump separate fuel until payment made for first and pump zeroed. Restart with same fuel is possible provided nozzle not replaced first. | A18 | Decide whether a timed cutoff should be included so restart is not possible after a selected time. | SM
21 | Other fuel container filled | Customer uses fuel can (perhaps as well as filling car fuel tank) | Pump is stopped and then restarted. May attempt to pump a different fuel. High-level cutoff may not work if container has a wide neck. | Not possible to pump separate fuel until payment made for first and pump zeroed. Restart with same fuel is possible provided nozzle not replaced first. | A19 | Check whether high-level cutoff works in wide necked containers. | PM
22 | Other event— carjacking attempted | Planned criminal activity | Risk of violence with injury (or death). | Warning to customers to remove car keys and not to leave car unlocked. | A20 | Check wording and prominence of notices. | HS
22 | Other event— carjacking attempted | Planned criminal activity | Risk of violence with injury (or death). | Warning to customers to remove car keys and not to leave car unlocked. | A20 | Check wording and prominence of notices. | LO
22 | Other event— carjacking attempted | Planned criminal activity | Bad publicity inevitable. | Warning to customers to remove car keys and not to leave car unlocked. | A21 | Put up clear notice that CCTV is in use as a deterrent. | SM
22 | Other event— carjacking attempted | Planned criminal activity | Risk of violence with injury (or death). | Warning to customers to remove car keys and not to leave car unlocked. | A22 | Review emergency procedures to ensure this eventuality is covered and that training is provided. | SM
22 | Other event— carjacking attempted | Planned criminal activity | Risk of violence with injury (or death). | Warning to customers to remove car keys and not to leave car unlocked. | A22 | Review emergency procedures to ensure this eventuality is covered and that training is provided. | LO